## Slide 1
Unit 106 Understand and demonstrate fundamental electrical installation operations
Outcome 5 Be able to select materials and components for basic electrical practical applications
Bob Eyre

## Slide 2
Objectives
5.1 select materials and components for basic electrical practical applications
5.2 select electrical materials used for fixing cables and components:
clips
fixing devices, ie screws

## Slide 3
Select materials and components for basic electrical practical applications
Although electrical design is more complex than the examples given at this level circuits are designed so that
  An appliance or circuit is able to safely consume the amount of electricity it is designed to
  A protective device is chosen that allows that amount of power to be consumed but not much more.
  The cables feeding that circuit are protected by thedevice we chose in the previous step.
Follow these steps and the circuit is healthy as
  The appliance works OK
  The wiring doesn’t overheat
  If a fault occurs the circuit disconnects quickly and safely.

## Slide 4
Select materials and components for basic electrical practical applications
As a very rough rule of thumb at this level use the following table to get an rough idea of how much power circuits use, the current drawn, protective device rating and likely cable size needed to feed it.
Circuit Description | Power (Watts) | Current (A) Watts/230V | Protective Device Rating (A) | Cable Size (mm)
Lights | 1,200 | 5.2 | 6 | 1.5
Immersion Heater | 3,000 | 13.04 | 16 | 2.5
Radial Sockets 20A |  |  | 20 | 2.5
Radial Sockets 32A |  |  | 32 | 4.0
Ring Circuit |  |  | 32 | 2.5
Cooker | 8,800 | 38.26 | 40 | 10
Shower | 10,000 | 43.47 | 45 | 10

## Slide 5
Select materials and components - lights
A lighting circuit would need
6A MCB
Light fittings (pendant sets)
Enough 1.5mm sq twin and cpc cable to go from the consumer unit to a light and from light to light plus from each light to its switch.
Earth sleeving and brown sleeving
Some back boxes for the switches
Some light switches
Screws and 1.5mm twin and cpc clips
some
Circuit Description | Power (Watts) | Current (A) Watts/230V | Protective Device Rating (A) | Cable Size (mm)
Lights | 1,200 | 5.2 | 6 | 1.5

## Slide 6
Select materials and components – Imm Heater
An immersion heater circuit would need
16A MCB
Immersion heater and thermostat
Enough 2.5mm sq twin and cpc cable to go from the consumer unit to the immersion heater switch
Earth sleeving (no brown sleeving needed)
A back box for the Immersion Switch
A 20A DP Immersion Heater Switch
Butyl Heat resistant flex
Screws and 2.5mm twin and cpc clips
some
Circuit Description | Power (Watts) | Current (A) Watts/230V | Protective Device Rating (A) | Cable Size (mm)
Immersion Heater | 3,000 | 13.04 | 16 | 2.5

## Slide 7
Select materials and components – Ring Circuit
A ring circuit would need
32A RCBO
Immersion heater and thermostat
Enough 2.5mm sq twin and cpc cable to go from the consumer to a skt fr to the immersion heater switch
Earth sleeving (no brown sleeving needed)
A back boxes for the switch
Immersion Heater Switch
Screws and 2.5mm twin and cpc clips
some
Circuit Description | Power (Watts) | Current (A) Watts/230V | Protective Device Rating (A) | Cable Size (mm)
Ring Circuit |  |  | 32 | 2.5

## Slide 8
Select materials and components – Shower
A 10kW shower circuit would need
45A RCBO
10kW Shower
Enough 10mm sq twin and cpc cable to go from the consumer unit to the shower switch and from the shower switch to the shower
Earth sleeving (no brown sleeving needed)
A 45A DP Shower Switch
A deep back box for the above switch
Screws and 10mm twin and cpc clips
some
Circuit Description | Power (Watts) | Current (A) Watts/230V | Protective Device Rating (A) | Cable Size (mm)
Shower | 10,000 | 43.47 | 45 | 10