## Slide 1
Circuit Design
(an intro)
Bob Eyre

## Slide 2
Objectives
To be aware of multiple factors that need to taken into account in designing a circuit such as
  selecting appropriate method of protecting the circuit
  selecting appropriate cable type and size.

## Slide 3
Warm-up Questions
What do fuses & breakers do?
What do RCDs do?
What current will trip/operate a 32A breaker?
Remember I²R losses?

## Slide 4
3 Main things to consider
Step | What | Why
1 | Current Carrying Capacity | Cables get hot when carrying current
2 | Voltage Drop | We want a decent voltage at the load
3 | Disconnection Time | We want the circuit protective device to operate quickly
Often the cable chosen in step 1 will suffice for steps 2 and 3 but not always.

## Slide 5
1 Current Carrying Capacity
Cables get hotter when carrying current.
The more current a given cable carries the hotter it gets.
A cable with a larger CSA will heat up less than a similar thinner cable.
Cables lose heat more easily if in a cool environment.
Cables find it difficult to lose heat if
  Surrounded by other cables also trying to lose heat.
  Surrounded by insulation.

## Slide 6
2 Voltage Drop
We want to try to limit the voltage drop in the circuits cables so as much of the full 230V as practical is available across the load.
We need to limit volt drop to
  3% or 6.9V on lights
  5% or 11.5V on other circuits
Voltage drop in the circuit cabling wastes electricity in the form of a low level heat (I²R losses).
Voltage drop is affected by a circuits length, its cables CSA and its design current.

## Slide 7
3 Disconnection Time
Circuits need to disconnect quickly in the event of a fault.
On TN earthed systems TNS or TNCS the times are 0.4 or 5 seconds depending whether sockets are fed or not.
Lower EFLI paths create larger fault currents causing fuses/breakers to operate more quickly.
The length and CSA of a circuits conductors affect EFLI readings.

## Slide 8
Rule of Thumb calcs
Certain circuits are often wired using rule of thumb calculations.
In relatively similar scenarios such as identical houses with identical layouts, identical lengths of circuits, identical boards and breakers and circuit routes this may make sense.
Be aware, often a seemingly minor change (such as adding thermal insulation) can have a large effect on cable needed for a circuit.

## Slide 9
Any Questions
On to Step 1 in more detail